### 

### Request for Quotation

#### (Part-B)

#### For

#### Supply of

#### " SUPPLY AND INSTALLATION OF DISTRIBUTION BOARD AT BEML LIMITED, BANGALORE COMPLEX "

#### Tender No. 6300034393

#### Tender Closing date: 29.10.2020, 16.00 Hours

#### To

## BEML Limited

**Event Service Provider:**

****

Vendor’s Time and Expenses: To be borne by the vendor

No representation would be entertained on any errors if found in the RFQ. However vendors to bring such errors / omissions to the notice of BEML for necessary corrective action

**Confidential Document: for limited circulation among the participants of e-bid event, for Annual requirement finalization for BEML to be conducted on “BEML SRM” Platform**

##### Exhibit - A

|  |  |  |  |  |
| --- | --- | --- | --- | --- |
| Tentative requirement of  **“SUPPLY AND INSTALLATION OF DISTRIBUTION BOARD AT BEML LIMITED, BANGALORE COMPLEX”**  Division: BEML, Bangalore Complex | | | | |
| **Requirement Specification** | | | | |
| **Sl. No.** | **Item Code** | **Item Name** | **UOM** | **Quantity** |
| **1.** |  | SUPPLY OF DISTRIBUTION BOARD AT BEML LIMITED, BANGALORE COMPLEX | **NO** | **1** |
| **2** |  | INSTALLATION OF DISTRIBUTION BOARD AT BEML LIMITED, BANGALORE COMPLEX | **AU** | **1** |
| **SUPPLY AND INSTALLATION OF DISTRIBUTION BOARD FOR ADMINISTRATIVE BLOCK.**  General Terms and Conditions:  1. Necessary materials, tools, equipments like welding m/c, cutting m/c, welding electrode etc., required for carrying out the work has to be brought by the contractor. However power supply shall be provided by BEML.  2. The contractor shall provide necessary personal protective equipments (PPE’s) for his workmen and all precautions to be taken during execution of work.  3. All workers being employed for the work shall be covered under statutory requirement of ESI.  4. All works to be carried out as directed and to the complete satisfaction of the engineer in-charge.  5. A guarantee of ONE year to be provided.  **INSTALLATION OF DISTRIBUTION BOARD ON FLOOR WITH MS ANGLE FRAME WORK OF REQUIRED SIZE OR PEDESTAL BRICK MASONARY WORK AS REQUIRED AS PER SITE CONDITIONS.**    **Note:**  1) The tendering process is E-Mode and TWO BID SYSTEM basis,  (a) Technical bid and (b) Commercial bid, both through SRM Portal. The firm to quote separately.  2) Please open the collaboration folder to view Tender Documents  3) Kindly go through all the tender documents and bid accordingly.  4) **In technical bid, firm should send completely filled in & signed “Annexure-A,B and C”/ Technical specification sheet filling their acceptance/remarks in vendor remarks Column preferably in your company Letter head. Apart from this tenderer requested to upload all relevant technical details like catalogue, drawing, make etc.**  **Kindly do not upload any commercial related documents in the Technical Bid If any commercial details in any form found in the technical bid, summarily rejecting the bid and further no correspondence will be entertained in this regard.**  **6) Please Provide Entire PRICE BREAK UP DETAILS in the BIDDER'S REMARK Section Only.**  7) Only the Technical bids will be opened first and will be sent for technical evaluation.  Commercial bids of technically qualified bidders only will be opened.  8) To be delivered to BEML Bangalore Complex on FOR basis.  9) A like to like comparison of Specifications & Notes of our tender enquiry w.r.t the offers to be furnished along with the offer.  10) Quotation should be valid for 120 days from date of tender opening.  11) FAX/E-mail/Manual quotations are not acceptable and quotations received through these modes will be rejected. Incomplete and conditional offers are also liable for rejection.  12) If any of the vendors have defaulted in supplies/services to BEML limited after placement of purchase order or If any of the vendors have backed out from their quotation submitted for the enquires of BEML limited or If any of the vendors have given wrong Information/documents to BEML Limited along with quotations, their quotation will not be considered and their quotation will be rejected. The quotations of the Firms who have not provided Service during the Warranty period of any product supplied by them to BEML Ltd will not be considered & will be rejected.  13) Corrigendum if any will be updated in BEML website only.  14) Any clarification in the tender, please contact in 080-25348770 / 25022638/ 25022635 Email ID: [rmm-1@beml.co.in](mailto:rmm-1@beml.co.in)  15) In case of technical difficulty in participation , kindly contact our cooperate office No 22963269 | | | | |
| **DELIVERY SCHEDULE** | | | | |
| **The above items are required from October 2020** | | | | | |

Signature Company Name:

Signed By Company Seal:

**Date:**

**Note: Vendors are requested to put seal and signature in Exhibit A indicating their acceptance to delivery schedule and submit the same to us in original letter head**