TENDER REF: 6300029905

PART A – TECHNICAL SPECIFICATIONS & CONDITIONS

Description :   Supply,  Installation  and  Commissioning of  500 KVA Silent Type Diesel Generator set.

Qty:  01 No.

Eligibility Criteria:

- The OEM or their Authorized dealers are eligible for participating in the tender.

- The authorized dealer shall submit authorization letter from their manufacturer at the time of quoting (Informative).

- The OEM shall submit relevant certificates for being a manufacturer.

- The firm has to supply latest version/model of the DG Set. (Make and Model of Engine and Alternator should be mentioned).

- The firm should have supplied and installed DG set of capacity minimum of 500 KVA and above rating. Supporting documents like Purchase Orders to be submitted (Informative).

- The firm has to submit previous Performance / Satisfactory Work Completion Certificates for a minimum of 02 years (Informative).

- The firm has to submit a list of supply of DG set to their clients with Supportive documents (PO copy).

Technical   Specifications:

Engine make:   Cummins, Mahindra, Kirloskar, Perkins, Ashok Leyland, Greaves, Volvo, Caterpillar, Tata..

Prime power rating:

KVA -500 Minimum

KW- 400 Minimum

BHP: Developing Minimum 590 BHP @1500 RPM under NTP conditions.

Voltage - 3phase, 415 Volts, 4 Wire (R Y B Neutral).

PF – 0.80.

Frequency – 50 Hz.

Current –Approximate 695 Amps.

RPM -1500.

Diesel Engine:

Number of Cylinders, Number of Strokes and Type of Engine

(IN-LINE or V-type): Shall be as per the OEM Design and Construction and same to be indicated.

Fuel Efficiency: 230 milligrams to 235 milligrams / KW / HOUR.

Speed Governing System – Electronic Type.

Coupling – Engine directly coupled to alternator.

Cooling system - Engine driven fan, radiator, radiator guard, thermostat and coolant pump.

Turbo charger and after cooler, Lubrication system, fuel system, Intake and Exhaust system, Cooling system, Starting system, Sensors, switches, Genset controller.

Starting of Generator system: - The Generator Should have Auto start/ stop facility and Manual start/ stop facility.  (Provision of AMF Panel is BEML’s Scope)

Starting system Battery –

12V, 180 AH, SMF Battery, Qty - 02 Nos.

Make: Exide / Amaron / Panasonic and

01 No. Battery charger unit.

Electronic instrument panel to display:  The DG set should have facility of displaying battery voltage, coolant water temp, oil pressure, engine speed, engine hours, high water temperature, low oil pressure, over speed, over Load ... etc. and all other engine and alternator protection devices/systems.

AC generator / Alternator:

Alternator Make – Stamford, Kirloskar, Cummins, Leroy somer, Crompton.

Suitable rating for 3 Phase, 4 Wire, 415 Volts, 0.8 PF, 50 Hz, 1500 RPM.

Alternator Type – Brushless, self-excited, self-regulated, single bearing type, with in-built AVR.

Mounting: The engine and AC generator/alternator shall be directly coupled, aligned and mounted on a rigid MS fabricated base frame with anti-vibration pads with Levelling.

Foundation & Earthing: The firm has to provide GA drawing immediately after receipt of PO. (Provision of Foundation & Earthing BEML Scope).

Peripherals: Fuel storage day tank with approximate 900 litres capacity, suitable silencer, exhaust flexible expansion bellow, 02 No’s of 12volts, 180 AH dry maintenance free batteries with leads,

01 No. Suitable capacity Battery charger.

Dimensions: L x W x H of the DG set including Acoustic Enclosure to be mentioned

Exhaust System: The firm has to make provision for Exhaust system with suitable silencer along with standard Length with mounting stand, as per requirement of Pollution control board norms.

Acoustic Enclosure: Made of high quality CRCA sheet steel, integral partitions, doors, rock wool of relevant thickness and density, with suction and discharge louvers and the enclosure construction shall provide sufficient access for maintenance.

All other standard accessories / fitments as per OEM.

Terms and Conditions

- BEML Scope of Works

- Foundation Bed.

- Earthing Pits.

- Power Cabling and

- AMF Panel Board.

- Documents

- Diesel Generator test certificates.

- Alternator test certificates.

- Operation & Maintenance Manuals (Two sets).

- Engine parts catalogue.

- Standards: Engine and Alternator shall be as per relevant BIS.

- Approval from relevant authorities: State / Central Pollution Control Board & if any other approval required is under firms’ scope.

- Warranty for DG Set: Two Years Warranty. During this period any part found defective shall be repaired / replaced by the firm at free of cost

- Warranty for Battery: Exide / Amaron / Panasonic make with three years warranty. During this period any part found defective shall be repaired / replaced by the firm at free of cost

- Spares & Service: The firm has to provide minimum of 10 years for service & spares support from the date of commissioning.

- Delivery: The Equipment to be delivered to BEML, Bangalore Complex.

The complete equipment along with all accessories / attachments shall be delivered within two months from the date of release of Purchase Order.

Commissioning: The firm should depute their service personnel for installation, commissioning and handing over of the D G Set and prove out the Satisfactory working with LOAD.

It should be the entire responsibility of the firm to supply, erect, install and commission, prove out the machine features and hand over to the entire satisfaction within the stipulated time from the receipt of the machine at BEML.

BEML will only provide power (electricity), material-handling facility required for the installation, rest of the things required for installation to be arranged by the firm.

The erection and commissioning should meet the provision of Factories Act as prevailing in India.

All the workmen being employed for erection and commissioning should be covered under ESI and necessary safety precautions should be taken by wearing personal protective equipment’s during commissioning

- Civil Works:  Foundation Bed is in BEML Scope.  However, Foundation GA Drawing to be submitted by the firm after release of P.O (at least one month before date of Dispatch).

- Publication:

  - Along with the offer the firm should furnish the original catalogue of Equipment and other standard accessories indicating all technical information / specifications along with the quotation.

  - Along with the equipment the firm should furnish the following publications Triplicate

- Diesel Generator Test Certificates

- Alternator Test Certificates

- Three sets of Operators & Maintenance Manuals (O &M)

- Engine Parts Catalogue

- After Sales Service:

BEML will not hold any inventory of spares required for the maintenance of the system.In case of breakdown; the firm should depute their service personnel within 24 hours along with necessary spares and set right the equipment within warranty period.

- The firm should furnish comparative statement /  Deviation  Statement of our tender enquiry  for  description,   specifications,  and  notes  vis-à-vis the model offered by them along with the offer.

- Inspection:  the equipment with accessories will be subject to acceptance by our divisional quality-engineering department  /  Electrical maintenance dept  at  BEML Site.

- Safety   Clauses  :   The  equipment  /  Machineries  supplied  satisfy  all  the  norms  of  State / Central  Pollution  Control  Board ,     ISO 14001, i.e., Protection  of  Environment,   Prevention  of  Pollution  and  Conservation of  Resources  and  also  ISO 18001,  i.e.,  ensure  Occupation  Health  and  Safety   like  prevention  of  personal  injury  and  ensure   safe  working  environment  and  If  any  other  approval  required  is  under firms  Scope

# Compliance to Technical specifications and Technical terms & conditions as per Annexure I [Mandatory]should be uploaded in SRM portal in the Technical bid.