### Request for Quotation

#### (Part-B)

#### For supply of

#### " RE-FURBISHMENT & UP-GRADATION OF END FEED UNITS FOR BBT”

#### Tender No. 6300028053

#### Tender Closing date:05.02.2020, 16:00 Hours

#### To

## BEML Limited

Vendor’s Time and Expenses: To be borne by the vendor

No representation would be entertained on any errors if found in the RFQ. However vendors to bring such errors / omissions to the notice of BEML for necessary corrective action

# Product Specific Information:

| Enquiry No.: |  | 6300028053 |  |
| --- | --- | --- | --- |
| Sl.No | Description |  | Qty. |
| 1 | Supply of 3cx240sqmm,11KV, XLPE Al. cable |  | 95.000 M |
| 2 | Making of trench in concrete 1.2M depth |  | 1AU |
| 3 | Laying of cable in trench & reconcreting |  | 1 AU |
| 4 | Supply of Hume pipes 150mm dia,2M length |  | 8 NO |
| 5 | Making / Installation of end termination |  | 1 AU |
| Standards Applicable |  | “As per Exhibit – A” |  |
| Delivery Schedule: |  | Please refer to “Exhibit – A” |  |
| Volume of Business |  | Total volume of business projected in “Exhibit-A” is a firm requirement. However volumes mentioned may vary substantially on either side depending on business needs. |  |
| Price Basis for the tender Event: |  | Bidder has to forward their quote in detail like Basic Price, Excise Duty and Sales Tax (CST or VAT) separately in the item data column which is applicable. . Bidding to take place on per Item basis Note: - Transit Insurance, Handling Charges, etc. to vendor’s account. - Bids placed by bidder shall be unconditional and complete in all respect in line with price basis described above. Any incomplete / non-compliant offers are subject to rejection. - Vendor should also take into account inspection charges of the inspection agency, which are to be absorbed by Vendor. |  |
| Business Share & Preference |  | - Buyer reserves the right on quantum of business on such sources. - In case ordering on multiple sources, BEML reserves the right to distribute the order on more than one source at the lowest bid price received against this bidding, on 60:40 / 50:30:20/40:30:20:10 ratios for allocation - Preference may be given to bidders bidding for the entire lot and are at the same time remain most competitive, technically suitable, meeting delivery requirements and proven sources. |  |
| Drawing/Specification |  | As per “Exhibit – A” |  |
| Supply Pattern: |  | Material to be supplied as detailed in section “Delivery Schedule” |  |
| Inspection Authority & Charges: |  | - Inspection by BEML at BEML Bangalore Complex. - The inspecting officer’s decision as regards the rejection shall be final and binding on the contractor |  |

##### Exhibit – A

| Tentative requirement of RE-FURBISHMENT & UP-GRADATION OF END FEED UNITS (SWITCHES) FOR MAIN BUS BAR TRUNKING (BBT) SYSTEM AT VARIOUS HANGARS Division: BEML, Bangalore Complex |  |  |  |
| --- | --- | --- | --- |
| Requirement Specification |  |  |  |
| Sl. No. | Item Name | UOM | Quantity |
| 1 | Supply of SDF unit panel 415V, 400A, 3p Supply of Switch Disconnector Fuse (S.D.F) with panel 415V, 400A, 3 pole complete with rated fuses in a sheet steel enclosure with top and bottom cable entry boxes suitable to accommodate 1 run x 400 sqmm LT cable. The enclosure shall be fabricated using 1.6mm thick CRCA sheet and shall be powder coated. The total dimension / size of the enclosure shall be Length: 1600mm, Width: 500 mm and Depth: 350mm. (i) Incoming cable entry (bottom) shall be 500mm x 500mm x 350mm with extended bus bars, hinged type door with panel type lock. (ii) Outgoing cable entry box (top) shall be 600mm x 500mm x 350mm with extended bus bars, hinged type door and panel type lock. This door shall accommodate RYB indication lamps, CT's of appropriate ratings, wiring .... etc., and Digital multifunctional meter to read voltage, current, frequency and KWHRS. (iii) 400 amps, SDF shall be accommodated in the enclosure 500mm x 500mm x 350mm space. The switch shall be front / side operated with indication lamps (R, Y, B) and multifunction Digital meter to read voltage, current, frequency and KWHRS. | No | 11 |
| 2 | Instn. of SDF unit panel 415V, 400A, 3p Installation of switch dis-connector fuse (SDF) panel on wall / steel column / pillars with necessary MS angle support brackets welded on to the pillars or fixing on the wall with necessary grouting bolts (as per the site requirement) 1 AU consists of Installation of 11 Nos of SDF | AU | 1 |
| 3 | Supply of 1.1KV, 3.5C x 400sqmm LT cable Supply of 1.1KV grade, 3.5 core x 400 sqmm LT cable, armoured and aluminium conductor, PVC sheathed & XLPE insulated. | M | 30.000 |
| 4 | Instn. of 1.1KV, 3.5C x 400sqmm LT cable Laying and installation of 3.5 core x 400 sqmm LT cable on walls / pillars …. etc., with necessary MS angle support brackets and cable to be neatly clamped. 1 AU of consists of installation of 30 m of cable | AU | 1 |
| 5 | Supply of LT end termination materials Supply of LT end termination materials like glands, lugs etc., suitable for 3.5 core x 400 sqmm LT cable | NO | 6.000 |
| 6 | Inst/making of LT end termination Making / installation of LT end termination for 3.5 core x 400 sqmm LT cable 1 AU consists of installation of 6 no LT end termination | AU | 1 |
| 7 | Dismantling/removing old 400A switch Dismantling / removing of old / defective 400 amps switch, which includes dis-connecting of existing cables incoming and outgoing, removal of bus bar chambers / boxes and other related works. 1 AU consists of installation of 11 no 400A switch | AU | 1 |
| RE-FURBISHMENT & UP-GRADATION OF END FEED UNITS (SWITCHES) FOR MAIN BUS BAR TRUNKING (BBT) SYSTEM AT VARIOUS HANGARS AT BEML LTD., BANGALORE COMPLEX. GENERAL TERMS & CONDITIONS: 1. The firm has to visit the site to ascertain the nature of work required. 2. All tools, equipments like welding machine, cutting machine, welding electrodes …. etc., required for the works are in contractor’s scope. Power supply to these machines shall be provided by BEML. 3. All safety measures / rules to be followed / adhered to by the contractor. 4. Labours to be covered under ESI / PF regulations. 5. Necessary power shutdown shall be arranged by BEML at a mutual convenient date preferably during Sundays / holidays so that production schedules are not affected. 6. BEML shall supply wherever required / necessary, copper flexible cables of suitable size along with lugs…. etc., for load side connection (from switch to BBT). 7. Necessary labelling / stencilling to be done on New switches for indication purpose. 8. wherever required, new LT end terminations to be carried out (as directed by Engineer-in-charge) 9. At few locations (as directed by Engineer-in-charge), the existing terminations of both incoming and outgoing cables shall be retained and connected. 10. Drawing of the panel board to be submitted for approval before taking up fabrication. 11. All works to be carried out as per the directions of Engineer-in-charge. NOTE:L1 status will be considered as 1 AU for RE-FURBISHMENT & UP-GRADATION OF END FEED UNITS (SWITCHES) FOR MAIN BUS BAR TRUNKING (BBT) SYSTEM AT VARIOUS HANGARS AT BEML LTD., BANGALORE COMPLEX Note: - The tendering process is E-Mode - You should have Digital Signature Certificate (class III) issued by authorized agencies to submit commercial bid on E-mode. - Please open the collaboration folder to view Tender Documents (PART A, PART B & covering letter) - Kindly go through all the tender documents and bid accordingly. - To be delivered to BEML Bangalore Complex on FOR basis. - Quotation should be valid for 120 days from date of tender opening. - FAX/E-mail/Manual quotations are not acceptable and quotations received through these modes will be rejected. Incomplete and conditional offers are also liable for rejection. - If any of the vendors have defaulted in supplies/services to BEML limited after placement of purchase order or If any of the vendors have backed out from their quotation submitted for the enquires of BEML limited or If any of the vendors have given wrong Information/documents to BEML Limited along with quotations, their quotation will not be considered and their quotation will be rejected. The quotations of the Firms who have not provided Service during the Warranty period of any product supplied by them to BEML Ltd will not be considered & will be rejected. - Corrigendum if any will be updated in BEML website only. - For any technical difficulty in submitting the Bid, please contact Mr.KrishnaMohan in the following numbers: 080-22963269 / 22963141. - Any clarification in the tender, please contact Mr. UDAY KUMAR in 080-25348770 / 25022638/25022635, E-Mail ID: rmm-1@beml.co.in Delivery : August- 2019 |  |  |  |

Signature						     Company Name:

Signed By						     Company Seal:

Date: